SECTION 14202

ELEVATORS AND LIFTS

Display hidden notes to specifier. (Don't know how? Click Here)

Copyright 2008 - 2017 ARCAT, Inc. - All rights reserved

** NOTE TO SPECIFIER ** Savaria ; residential and commercial elevators and lifts.
 .
 This section is based on the products of Savaria, which is located at:
2 Walker Drive  
Brampton, ON, Canada L6T 5E1
Toll Free Tel: 800-661-5112
Tel: 905-791-5555
Fax: 905-791-2222
Email: request info
Web: www.savaria.com

[ Click Here ] for additional information.

As a leading designer and manufacturer of residential elevators, luxury home elevators, commercial elevators and lifts for over 30 years, Savaria Lifts has thousands of satisfied customers to thank for their business.  Our global operation continuously seeks to advance manufacturing processes in our own modern facilities, allowing us to offer exceptional value and shorter lead times, while never compromising product quality, safety or reliability.  As an active member of many trade associations, we are committed to the ongoing support of its customers and dealers alike. Authorized dealers are carefully selected for their knowledge and experience, kept up-to-date with the latest technical and training sessions, and supported with our expert customer service.

Residential Elevators: Easily and quickly installed in new or existing homes, our residential elevators will embellish your home decor with its many available stylish finishes.

Savaria Infinity Luxury Elevator: Designed to provide a luxurious yet affordable means of vertical transportation for multilevel homes. Infinity's reliable, quiet and smooth operation is ensured by our innovative hydraulic drive system. With a variety of cab finishes and colors the Infinity allows you to customize your design for a more personalized look.
Savaria Eclipse Home Elevator: This machine room-less design saves space in the home and can also reduce installation time. With an extensive selection in custom finishes, the Eclipse elevator can be designed to suit almost any tastes and preferences.

Savaria Vuelift Elevator: Vuelift integrates into beautiful households both seamlessly and tastefully. Utilizing an integrated full glass hoistway and completely self-contained design, a Vuelift provides a power and precision unrivaled in the marketplace. Vuelift elevators come in two styles to match the architecture of your home: the trademark original round elevator with sweeping curved cylindrical glass, or the sleek octagonal glass elevator with unique folded corner design.

Commercial LU/LA Elevator:   Savaria provides user-friendly, good value solutions for both new construction, and retrofitting into existing buildings.

Savaria Orion LU/LA: A fully enclosed commercial elevator that makes code compliance fast and easy. Completely redesigned, it meets all current American and Canadian Code requirements for limited-use/ limited application (LU/LA) elevators. It is also suitable for residential use.

Commercial Wheelchair Lifts:

Savaria Prolift SCL: A fully enclosed Commercial Lift that provides an economical means of vertical transportation for the physically disabled. It has a reliable, quiet, and smooth operation while serving from two to four floors.

V1504: The unique drive and platform combinations of the V-1504 vertical wheel chair platform lift allows for rapid delivery and ease of installation in respect to any architectural requirements.

Multilift Vertical Platform Lift: The ACME screw drive system offers a safe and reliable operation for its users. This ruggedly constructed lift has been proven for both indoor and outdoor applications. The Multilift vertical wheel chair platform lift is designed to meet today's safety code requirements such as ASME A18.1 for residential and commercial use.

- GENERAL

  - SECTION INCLUDES

** NOTE TO SPECIFIER ** Delete items below not required for project.

    - Residential elevators.

  - RELATED SECTIONS

** NOTE TO SPECIFIER ** Delete any sections below not relevant for elevator products; add others as required.

    - Division 16 Sections for electrical service for elevators to and including disconnect and fused switches at machine room.

    - Division 16 Sections for standby power source, transfer switch, and connection from auxiliary contacts in transfer switch to controller.

    - Division 16 Section "Voice and Data Communication Cabling" for telephone service to elevators.

    - Section 03300 - Cast-in-Place Concrete: Concrete for elevator machine foundation, and pit.

    - Section 06100 - Rough Carpentry: Hoistway framing, building-in hoistway door frames and overhead hoist beams.

    - Section 08210 - Wood Doors: Hoistway doors.

    - Section 08710 - Door Hardware.

    - Section 09260 - Gypsum Board Assemblies: Gypsum shaft walls.

    - Section 09650 - Resilient Flooring: Floor finish in cab.

    - Section 09686 - Carpet: Floor finish in cab.

    - Section 09900 - Paints and Coatings: Interior transparent wood finish in cab.

    - Section 13850 - Detection and Alarm: Fire and smoke detectors and interconnecting devices.

  - REFERENCES

** NOTE TO SPECIFIER ** Delete references from the list below that are not required.

    - American National Standards Institute (ANSI) B-29.2 - Chain Standards for Inverted Tooth (Silent) Chains and Sprockets.

    - American Society of Mechanical Engineers (ASME) A17.1 - Safety Code for Elevators and Escalators.

    - American Society of Mechanical Engineers (ASME) A18.1 - Safety Standard for Platform and Stairway Chair Lifts.

    - CSA B44.1 - Elevator and Escalator Electrical Equipment.

    - CSA B355 - Lifts for Persons with Physical Disabilities.

    - CSA B613 - Private Residence Lifts for Persons with Physical Disabilities.

    - U.S. Architectural & Transportation Barriers Compliance Board's "Americans with Disabilities Act (ADA), Accessibility Guidelines for Buildings and Facilities (ADAAG)".

    - ICC/ANSI A117.1 - Accessible and Usable Buildings and Facilities.

    - NFPA 70 - National Electric Code.

    - CSA - National Electric Code.

  - REQUIREMENTS OF REGULATORY AGENCIES

    - Fabricate and install work in compliance with applicable jurisdictional authorities.

    - File shop drawings and submissions with local authorities as the information is made available. Company pre-inspection and jurisdictional authority inspections and permits are to be made on timely basis as required.

  - SUBMITTALS

    - Submit under provisions of Section 01300.

    - Product Data: Manufacturer's data sheets on each product to be used, including:

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Installation methods.

    - Shop Drawings: Provide a complete layout of lift equipment detailing dimensions and clearances as required.

** NOTE TO SPECIFIER ** Delete selection samples if colors have already been selected.

    - Selection Samples: For each finish product specified requiring selection of color or finish, two complete sets of color charts representing manufacturer's full range of available colors and patterns.

  - QUALITY ASSURANCE

    - Installer Qualifications:  Minimum 2 years of experience installing similar products, and acceptable to the manufacturer.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in manufacturer's unopened packaging until ready for installation.

  - PROJECT CONDITIONS

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install systems under environmental conditions outside manufacturer's recommended limits.

  - WARRANTY

    - Provide manufacturer’s standard 36-month limited warranty on parts from date of shipment.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer:  Savaria, which is located at: 2 Walker Drive, Brampton, ON, Canada, L6T 5E1; Toll Free Tel: 800-661-5112; Tel: 905-791-5555; Fax:  905-791-2222; Email: request info; Web: www.savaria.com

** NOTE TO SPECIFIER ** Delete one of the following three paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

    - Substitutions: Not permitted.

    - Requests for substitutions will be considered in accordance with provisions of Section 01600.

  - RESIDENTIAL ELEVATOR

    - Residential Elevator: Savaria Vuelift Round and Octagonal

      - Model:

** NOTE TO SPECIFIER ** Please select model type

- Vuelift - Round

- Vuelift - Octagonal

    - Equipment: Provide equipment, incidental material and labor required for complete, operable winding drum elevator installation. The elevators shall be erected, installed, adjusted, tested and placed in operation by the elevator system manufacturer or manufacturer's authorized installer.

    - Performance: The elevator shall be designed and tested in accordance with ASME A17.1 Section 5.3. The testing shall consist of loading the platform to rated capacity for several cycles to insure proper operation. Mechanical failures and defects shall be corrected.

    - The following preparatory work to receive the elevator specified shall be the work provided by others:

      - Permanent 230 VAC, 30 amp single phase power to operate lift to be provided from a lockable fused/cartridge type disconnect switch with auxiliary contacts for battery operation. 115 VAC, 15 amp single phase power to operate the lighting circuit. Refer to Drawings for permanent power specifications and location of disconnects. Temporary power may be provided to expedite installation of lift.

      - Finished floors including floor cutouts at landings

      - Working telephone jack near the electrical disconnects

      - Provide substantial, level pit floor slab as indicated on the lift contractor's shop drawings

    - Characteristics:

      - Rated Load:

** NOTE TO SPECIFIER ** Delete rated load not required. For Round model, option ‘a’ must be chosen.

- 840 lbs (341 kg)

- 950 lbs (431 kg)

      - Rated Speed:

** NOTE TO SPECIFIER ** Delete rated speed not required. Choose option ‘a’ for rated load of 840 lbs (341 kg) and option ‘b’ for 950 lbs (431 kg)

- 32 fpm (0.16 m/s).

- 40 fpm (0.20 m/s).

      - Car Floor Area:

** NOTE TO SPECIFIER ** Delete Car Floor Area size not required.

- 11.91 sq.ft. (1.11sq.m.) – Octagonal Model Only

- 12.41 sq.ft. (1.25 sq.m.) – Round Model Only

** NOTE TO SPECIFIER ** Delete Car height size not required. First option fits in overhead of 108 inches (2743mm) and the second option fits in an overhead of 96 inches (2438mm)

      - Car height:

        - 84 inches (2134 mm) (standard)

        - 76.5 inches (1943 mm)

      - Operation: Automatic.

      - Power supply: 230 Volt, Single Phase, 30 Amps.

** NOTE TO SPECIFIER ** Please enter travel height

      - Travel: ______ feet. Maximum of 42.5 feet (510 inches).

      - Levels Serviced:

** NOTE TO SPECIFIER ** Delete number of levels not required.

- Levels: 2.

- Levels: 3.

- Levels: 4.

- Levels: 5.

- Levels: 6.

      - Cab Configuration:

** NOTE TO SPECIFIER ** Delete cab configurations not required.

- Enter/exit same side.

- Straight through cab

- 90 degree

      - Lighting supply: 115 Volt, 1 Phase, 15 Amps.

      - Galvanized aircraft cable suspension 2 x 3/8 inch (9.5 mm) diameter

      - Drive: Pre-programmed variable frequency for smooth start and stops

      - Car operating panel: Automatic push buttons, and emergency stop/alarm button.

      - Phone: Integrated phone with keypad and speaker

      - Hall call stations: Provide a keyless hall call station with an illuminated call button and a matching cover plate for each landing.

      - Emergency operation: The car shall be equipped with a battery-operated light fixture, emergency battery lowering device and alarm in case of normal building supply failure. The battery shall be the rechargeable type with an automatic recharging system. A manual lowering device shall be located in a lockable box positioned at the uppermost landing.

      - Pit Depth:

** NOTE TO SPECIFIER ** Delete options for pit depth not required. Additional pit may be required in some jurisdictions.

        - A 4 inch (101.6 mm) recessed pit will be required for a level bottom landing finish (standard)

        - No pit; a 3” ramp will be included with the elevator

    - Cab Enclosure:

- Walls:

** NOTE TO SPECIFIER ** Delete options for walls not required. Option ‘b’ must be chosen for 950 lbs (431 kg) rated load model, otherwise, option ‘a’ must be chosen.

        - Textured powder coated steel frame with acrylic panels

        - Textured powder coated steel frame with low iron laminated silica glass panels

- Ceiling

** NOTE TO SPECIFIER ** Delete options for Ceiling not required.

        - Textured powder coated steel - standard

        - Panoramic car ceiling - optional

- Overhead lights in the car compartment shall turn ON automatically when the elevator door is opened and stay on while the elevator is in use. The elevator lights will shut off by a timer when the elevator is not in use.

Elevator lighting shall be provided by: recessed energy saving led cab lights

- Cab floor: Unfinished 3/4 inch (19 mm) plywood sub-flooring with carpet.

- Car gate: Manual bifold Gate

    - Hoistway:

- Hoistway Finish:

** NOTE TO SPECIFIER ** Delete options for Hoistway Finish not required. Option ‘b’ must be chosen for 950 lbs (431 kg) rated load model, otherwise, option ‘a’ must be chosen.

        - Textured powder coated steel frame with acrylic panels

        - Textured powder coated steel frame with low iron laminated silica glass panels

- Landing doors: Clear vision manual swing-out doors

    - Systems and Components:

      - Machine Room: Required, controller outside hoistway.

      - The controller shall be pre-wired and tested prior to shipment. It will incorporate the following features.

        - Smooth stops at each landing.

        - Automatic battery back-up to ensure the lift can travel to lower landing in the event of a power failure.

      - Drivetrain: Winding Drum

      - Motor:

** NOTE TO SPECIFIER ** Delete options for Motor not required. Choose option ‘a’ for 840 lbs (341 kg) and option ’b’ for 950 lbs (431 kg)

        - 1.5 HP with integrated brake

        - 3 HP with integrated brake

      - Transmission: Ultra-low vibration 3-stage right angle helical bevel drive

        - All limit switches and leveling device switches shall be located in a position to be inaccessible to unauthorized persons. The switches shall be located in the hoistway.

      - Wiring and electrical connections shall comply with applicable codes. Insulated wiring shall have flame-retardant and moisture-proof outer covering and shall be run in conduit or electrical wire way if located outside the unit enclosure. Quick disconnect harnesses shall be used when possible.

      - The door locks shall be a CSA and UL approved electrical mechanical elevator interlock: Honeywell RDI-G L5B Certified with applicable codes

    - Emergency Devices:

      - Terminal limits. Stops the elevator if it overruns the normal limits at the top or bottom landing.

      - Final limits. A redundant safety feature if the elevator overruns the terminal limits at the top or bottom, the final limit stops the elevator and renders all automatic controls inoperable. If this happens, the elevator must be serviced to determine and correct the fault.

      - Pit switch. Disables elevator for servicing purposes.

      - Interlocks. Hoistway doors remain locked when the car is not at that floor and prevent the elevator from running until all doors are closed and locked.

      - 4 Type A Instantaneous Safeties in compliance with ASME A17.1 Sections 2.17.8.1 & 2.17.5.1 for instantaneous breaking in case of free fall or overspeed.

- EXECUTION

  - EXAMINATION

    - Do not begin installation until hoistway and machine room has been properly prepared.

    - Site dimensions shall be taken to verify that tolerances and clearances have been maintained and meet local regulations.

    - If substrate preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

  - PREPARATION

    - Clean surfaces thoroughly prior to installation.

    - Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

** NOTE TO SPECIFIER ** Delete if not required.

  - ELEVATOR INSTALLATION

    - Install in accordance with manufacturer's instructions.

    - Install the components of the elevator system that are required and that are required by jurisdictional authorities to license the elevator.

    - Trained employees of the elevator contractor shall perform installation work.

    - Adjust elevator for proper operation and clean unit thoroughly.

    - Instruct users in operating procedures and owner's maintenance person in trouble-shooting and maintenance procedures.

** NOTE TO SPECIFIER ** Delete if not required.

  - LIFT INSTALLATION

    - Install all the components of the lift system that are specified in this section to be provided, and that are required by jurisdictional authorities to license the lift.

    - Trained employees of the lift contractor shall perform all installation work of this section.

    - Adjust lift for proper operation and clean unit thoroughly.

    - Instruct users in operation procedures and Owner's maintenance person in trouble-shooting and maintenance procedures.

  - PROTECTION

    - Protect installed products until completion of project.

    - Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION